## Example
This is an example of calculation of the normalized performance characteristic curves of a heat pump for space heating.
For the calculation, data from a commercial heat pump provided by the manufacturer is taken as a reference (Viessmann, 2020).
Normalization is done considering a supply temperature of 35°C and a outdoor air temperature of 7°C as a reference point.
REFERENCES: Viessmann, 2020. “Dati integrativi pompe di calore VITOCAL 250-S per il calcolo delle prestazioni energetiche degli edifici, secondo UNI/TS 11300 parte 4”.
| Supply 35 °C |  | Supply 45 °C |  | Supply 55 °C
Toutdoor °C | kW | COP | kW | COP | kW | COP
-7 | 9.57 | 3.08 | 8.77 | 2.44 | 7.96 | 1.99
-2 | 10.01 | 3.54 | 9.17 | 2.38 | 8.33 | 2.02
2 | 10.92 | 3.77 | 10.01 | 2.71 | 9.08 | 2.09
7 | 15 | 4.5 | 13.75 | 3.38 | 12.48 | 2.45
12 | 15.8 | 4.81 | 14.48 | 3.61 | 13.14 | 2.62
NORMALIZED DATA
| Supply 35 °C |  | Supply 45 °C |  | Supply 55 °C
Toutdoor °C | kW | COP | kW | COP | kW | COP
-7 | 0.638 | 0.68444 | 0.58467 | 0.54222 | 0.53067 | 0.44222
-2 | 0.66733 | 0.78667 | 0.61133 | 0.52889 | 0.55533 | 0.44889
2 | 0.728 | 0.83778 | 0.66733 | 0.60222 | 0.60533 | 0.46444
7 | 1 | 1 | 0.91667 | 0.75111 | 0.832 | 0.54444
12 | 1.0533 | 1.0689 | 0.96533 | 0.80222 | 0.876 | 0.58222